SECTION 08 42 33 – REVOLVING DOOR ENTRANCES

- GENERAL

  - SUMMARY

- NOTE:  Edit this specification as required for the project

    - This section includes the following types of revolving entrance doors:

      - Two wing, automatic revolving door including enclosure walls and canopy.

    - Related Sections:

      - Division 7 Sections for caulking to the extent not specified in this section.

      - [Division 8 Section “Aluminum-Framed Entrances and Storefronts” for entrances furnished separately in Division 8 Section.]

      - [Division 8 Section “Door Hardware” for hardware to the extent not specified in this Section.]

      - Division 8 Section “Glazing” for materials and installation requirements of glazing.

      - Division 26 Sections for electrical connections including conduit and wiring for revolving door entrance operators and lighting.

  - REFERENCES

    - References:  Refer to the version year adopted by the Authority Having Jurisdiction.

      - ANSI A117.1 - Accessible and Usable Buildings and Facilities.

      - ICC/IBC - International Building Code.

      - NFPA 70 - National Electrical Code.

      - NFPA 101 - Life Safety Code.

    - American National Standards Institute (ANSI) / Builders Hardware Manufacturers Association (BHMA).

      - ANSI/BHMA A156.27 American National Standard for Power and Manual Operated Revolving Pedestrian Doors.

      - ANSI Z97.1 Standards for Safety Glazing Material Used in Buildings.

    - American Society for Testing and Materials (ASTM).

      - ASTM B221 Standard Specification for Aluminum and Aluminum Alloy Extruded Bars, Rods, Wire, Profiles and Tubes.

      - ASTM B209 Standard Specification for Aluminum and Aluminum Alloy Sheet and Plate.

    - American Architectural Manufacturers Association (AAMA).

      - AAMA 611 Voluntary Specification for Anodized Architectural Aluminum.

    - National Association of Architectural Metal Manufacturers (NAAMM).

      - Metal Finishes Manual for Architectural Metal Products.

    - International Code Council (ICC).

      - [IBC:  International Building Code Building Code.]

      - [CBC: California Building Code.]

  - DEFINITIONS

    - Activation Device: Device that, when actuated, sends an electrical signal to the door operator to activate the operation of the door.

    - Safety Device: A device that detects the presence of an object or person within a zone where contact could occur and provides a signal to stop the movement of the door.

  - PERFORMANCE REQUIREMENTS

    - Compliance with the following:

      - ANSI/BHMA A156.27 American National Standard for Power and Manual Operated Revolving Pedestrian Doors.

    - Thermal Movements:  Provide revolving entrance doors that allow for thermal movements resulting from maximum change in ambient and surface temperatures by preventing buckling, opening of joints, overstressing of components, failure of joint sealants, failure of connections, and other detrimental effects.  Base engineering calculation on surface temperatures of materials due to both solar heat gain and nighttime-sky heat loss.

    - Operating Temperature Range: -22 F to 130 F (-29 C to 54 C).

    - Emergency Exit door requirements: Comply with requirements of authorities having jurisdiction for revolving entrance doors serving as a required means of egress.

    - Breakout Force Requirements:

      - Revolving doors shall be provided with a mechanism that allows emergency breakout of door panels when a maximum force of 130 lbs (570 N) applied 3 inches (75 mm) from the outer edge of the door panel and 40 inches (1020 mm) above the floor, unless otherwise allowed by ANSI/BHMA A156.27.

    - Revolving door entrances shall have a mechanism that controls the speed of the rotating door panels to the maximum allowable revolutions per minute (RPM) as specified by ANSI/BHMA A156.27.

  - SUBMITTALS

    - Product Data:  Manufacturer's product data sheets including installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions and finishes.

    - Shop Drawings:  Submit manufacturer’s shop drawings, including elevations, sections and details, indicating dimensions, materials, and fabrication of doors, enclosure wall, canopy, operator, activation sensors, safety sensors, anchors, hardware, finish, options and accessories.

    - Samples: Submit manufacturer’s samples of aluminum finish.

    - Informational Submittals:  Manufacturer's product information and applicable sustainability program credits that are available to contribute towards a LEED rated project certification.

      - Credit MR 4.1 and 4.2: Manufacturer's or fabricator's certificate indicating percentage of post-consumer recycled content by weight and pre-consumer recycled content by weight for each Product specified under this Section.

    - Manufacturers Field Reports:  Submit manufacturer’s field reports from AAADM certified technician of inspection and approval of doors for compliance with ANSI/BHMA A156.27 after completion of installation.

    - Operating and Maintenance Manuals:  Provide manufacturers operating and maintenance manuals for each item comprising the complete door opening installation in quantity as required in Division 01, Closeout Submittals.  The manual to include the name, address, and contact information of the manufacturers providing the entrance and their nearest service representatives.  The final copies delivered after completion of the installation test to include spare parts list.

    - Warranties and Maintenance:  Special warranties and maintenance agreements specified in this Section.

  - QUALITY ASSURANCE

    - Manufacturers Qualifications:  Engage a qualified manufacturer with a minimum of ten (10) years of documented experience in manufacturing revolving door systems similar to that indicated for this Project and that have a proven record of successful in-service performance.

    - Installer Qualifications:  Installers, trained by the primary product manufacturers, with a minimum three (3) years documented experience installing and maintenance of units similar in material, design, and extent to that indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.

    - Certified Inspector Qualifications: Certified by AAADM.

    - Source Limitations for Revolving Door Entrances:  Obtain each type of door, frame, operator and sensor components specified in this Section from a single source, same manufacturer unless otherwise indicated.

  - PROJECT CONDITIONS

    - Field Measurements:  Verify actual dimensions of openings to receive revolving door entrances by field measurements before fabrication and indicate on shop drawings.

  - COORDINATION

    - Coordinate sizes and locations of recesses in concrete floors for recessed tracks and thresholds if applicable. Concrete work is specified in Division 03.

    - Electrical System Roughing-in: Coordinate layout and installation of revolving door entrances with connections to the electrical systems including fire detection and access control systems as applicable.

  - WARRANTY

    - General Warranty:  Reference Division 01, General Requirements.  Special warranties specified in this Article shall not deprive Owner of other rights Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

    - Revolving Door Entrances shall be free of defects in material and workmanship for a period of One (1) year from the date of substantial completion.

    - During the warranty period a factory-trained technician shall perform service and affect repairs. An inspection shall be performed after each adjustment or repair.

    - During the warranty period all warranty work, including but not limited to emergency service, shall be performed during normal business hours.

    - Manufacturer shall have in place a dispatch procedure that shall be available 24 hours a Day, 7 Days a week for emergency call back service.

- PRODUCTS

  - MANUFACTURER

    - Manufacturer:  ASSA ABLOY Entrance Systems, 1900 Airport Road, Monroe, NC 28110. Toll Free (877) SPEC-123.  Fax (704 ) 290- 5555 Website www.assaabloyentrance.us contact: specdesk.na.entrance@assaabloy.com

- NOTE:  Revise the following substitution clause as required by project requirements.  Select either Item “B” or “C”

    - [Substitutions:  Requests for substitution and product approval in compliance with the specifications must be submitted in writing and in accordance with the procedures outlined in Division 1, Section “Substitution Procedures”.  Approval of requests is at the discretion of the architect, owner, and their designated consultants.]

    - [Substitutions:  Not Permitted.]

  - REVOLVING DOOR ENTRANCES

    - Revolving door entrances including the following:

      - Aluminum framed glass revolving doors.

      - Radiused enclosure walls.

      - Entrance canopy and roof.

      - Overhead concealed electro-mechanical operator.

      - Microprocessor controlled revolving door control system.

      - Controls and accessories as required for a complete installation.

    - ASSA ABLOY UniTurn automatic revolving door entrances. (Basis of Design):

      - Two wing, automatic revolving door.

      - The nominal inside diameter of the revolving door entrance shall be as indicated.

        - [12’ diameter.]  [14’ diameter.]  [16’ diameter.]  [18’ diameter.]

      - Automatic operation, two-way pedestrian traffic.

      - Rotation:  Counterclockwise rotation.

      - Emergency escape doors.

        - Configuration:  Perimeter driven (no center shaft) revolving door with two double acting swing door panels.

        - Emergency Breakaway Capability:  Door panels shall breakout in the direction of egress.

  - REVOLVING DOOR ENTRANCE COMPONENTS

    - Two Wing Revolving Door Entrances:

      - Circular Enclosure Walls and Canopy:   Aluminum extrusion framing with a minimum wall thickness of 0.125 inches.   Framing for the enclosure walls and canopy shall be formed to the required radius. All internal structural support shall be I-beam construction.  A minimum of eight (8) vertical structural posts shall be provided.

        - Segmented walls and canopy shall not be allowed.

        - Metal-wrapped wood substrate or other metal-wrapped material substrates shall not be allowed.

      - Rotating Wings:   Aluminum extrusion framed glass panels.

      - Emergency Escape Doors:  Doors in rotating wings shall be as follows:

        - [One (1) pair of equal sized, double acting swing doors across the center of the opening.  Door wings shall be electro-mechanically locked in position.]

        - [One (1) pair of equal sized, power operated bi-parting sliding doors across the center of the opening.  Sliding doors shall be electro-mechanically locked in position.]

          - Provide remote activation switch for sliding door operation.

      - Weather Stripping:  Natural horse hair and synthetic fiber brush shall provide continuous horizontal and vertical seals during both the rotating mode and the non-rotating closed position to insure limited air infiltration.

      - Canopy:  Manufacturer's standard canopy construction, size and layout matching diameter of enclosure walls, with formed metal panel sides of material and finish matching enclosure walls, unless otherwise indicated.

        - The roof structure of the canopy shall be 5/8 inch laminated wood covered by a waterproof EPDM membrane, and shall include a water diversion system to drain roof water.

- NOTE:  Consult SpecDesk for metal roof options

        - [Aluminum sheet roof, finish as indicated.]

      - Rotating Ceiling:  5/8” laminate faced insulation board.

      - Ceiling Lights:  5 watt, 3000K LED MR16 lamp.   Flush mounted ceiling light fixtures in quantity as indicated.  (203-220VAC, AC light fixtures shall not be acceptable).

        - Light activation control via the program selection switch or from optional remote location.

- NOTE:  Select 10 LED fixtures for 12’ and 14’ diameter revolving doors

        - [Ten (10) LED light fixtures.]

- NOTE:  Select 12 LED fixtures for 16’ and 18’ diameter revolving doors

        - [Twelve (12) LED light fixtures.]

      - Glass:  Glazing shall comply with ANSI Z97.1, thickness as indicated.

        - Rotating section and double acting swing doors shall be 1/4" (6 mm) clear laminated glass.

        - Curved walls and curved rotating doors shall be 7/16" (11 mm) clear laminated glass formed to the required radius to assure a weather seal throughout enclosure.

          - Flat glass and segmented glass shall not be accepted in the radiused enclosure walls.

          - Butt glazed panels shall not be acceptable.

          - Plastic glazing material shall not be acceptable.

- NOTE:  Consult SpecDesk for heater options and details

  - REVOLVING DOOR OPERATOR AND CONTROLS

    - Controls must be microprocessor based "plug-in type" electronics (hard wired systems are not acceptable) with self-diagnostics and digital display status indicator.  Digital display status indicator must be located on the interior left of the curved outside wall system. System must be capable of providing information indicating door status, source or probable cause plus remedy.

    - Two Wing Revolving Door Operator and Controls:

      - Drive Assembly:  Perimeter-drive assembly with two 1/4 HP DC motors firmly attached to the internal rotating structural framing system. Motor drive wheels shall rotate on a fixed ring, and move ceiling and rotating wing assembly uniformly.

        - Positive braking and stopping shall be performed by two (2) magnetic disc brake and wheel assemblies.

        - Doors with center shaft or centrally AC motor driven gear/chain/belt mechanisms will not be allowed.

        - Power Requirements:  208-220VAC, 20 Amp, 60HZ line.

      - Self-Monitoring Function:  Supervision of all systems including safety sensors must be performed by the Micro-processor Control Unit (MCU) by conducting "self-monitoring" continuously.  Malfunction of any device shall cause the door to stop and the error code shall be indicated on the diagnostic display of the Micro-processor Control Unit MCU.

        - Revolving doors without the "self-monitoring function" will be considered unsafe and will not be acceptable.

      - Program Control Device (PCD):

        - Provide one (1) program control device (PCD) on the interior left vertical jamb of the curved wall. PCD shall provide eight (8) function capability including locked in closed position, entry/exit with start from closed position, entry/exit with start from open position, continuous rotation, exit only with start from open position, exit only with start from closed position, manual operation/forward, manual operation/reverse and summer position.

        - The PCD utilizes entry code access and does not require key operation during normal use of the door system.

        - The PCD incorporates a circular buffer memory that records the last 600 operational events of the door system and uses visual displays to notify the user when planned maintenance should be performed, if the real time clock and climate control systems are activated and if manual key lockout is in effect.

        - The real time clock is programmable for 3 different day schedules, 10 different operation modes per day schedule, weekly schedules and up to 16 exceptions for holidays.

        - The PCD can also accommodate remote diagnostics via an optional modem and client supplied telephone/data line.

  - ACTIVATION AND SAFETY CONTROL DEVICES

    - Two Wing Revolving Door Activation and Safety Devices:

      - Activation Devices:

        - Revolving door shall be activated by manufacturer's standard flush-mounted concealed motion sensors.  Activation units shall be solid state infrared technology.  Activation units shall be concealed in the fixed ceiling area directly above throat opening.

          - Two activation units per throat opening.

          - Surface mounted motion detectors shall not be acceptable.

        - Automatic Operation:  Signal from activation device activates unit and revolves door for one turn.  The unit shall then return to the closed position with the perimeter display wings closing the throat openings to the enclosure.

      - Safety Control Devices:

        - Primary and/or secondary safety devices located vertically on the outer edge of the rotating wing, horizontally on the wing panels, vertically at the entrances.  Devices shall include touchless, zone supervised Photocell Direct Reflection (PDR) and compressible safety switches.  All devices shall be incorporated as follows:

          - Vertical Safety Sensors:

            - Two (2) no-touch Photocell Direct Reflection (PDR) sensors covering the area immediately adjacent to the enclosure wall leading edges and must include zone-supervision.  Activation of the Photocell Direct Reflection (PDR) within the programmed safety zone shall cause the door to stop.

            - Two (2) no-touch rotating PDR sensors placed on the leading edges of the rotating wings. Activation shall cause the door to stop.

            - Two (2) compressible safety switches on the leading edges of the rotating wings. Activation shall cause the door to stop.

          - Horizontal Safety Sensors:

            - Two (2) no-touch Time Of Flight (TOF) infrared sensors placed in the ceiling covering the rotating door panel.  Activation of the safety sensors caused by an object being detected within 8 inches from the surface of the wing panel shall cause the door to stop or slow rotation.  Door will resume normal speed when the object is removed.

            - Four (4) compressible safety switches shall be placed on the bottom edge of the wing panels.  Activation shall cause the door to stop.

          - Emergency Stop:

            - The revolving door shall include two emergency stop push buttons on the curved enclosure per ANSI/BHMA A156.27.  When the button is pressed, the rotation shall stop.

          - Slow Speed Push Plates:

            - The revolving door shall include two (2) “push to slow” push plates.  When the push plate is pressed, the rotation speed will be reduced.

- NOTE:  Coordinate emergency escape door operation with the type of emergency escape door retained above.  Item 1 below applies to swing doors; Item 2 applies to power operated sliding doors only

      - Emergency Escape Operation:

        - Loss of power and/or fire alarm input shall be monitored by the MCU and its emergency battery unit.  Activation of the emergency battery unit shall cause the revolving door to rotate to the emergency position.

          - Revolving doors that do not rotate to the emergency position during a power failure will not be acceptable.

        - [The center double swing door panels shall be fitted with friction bar stabilizer system and power cut-off safety switches.  Door panels shall be held in place by electro-mechanical locking device and released upon fire alarm input or loss of power.]

          - Upon release of the electro-mechanical locking device, the swing doors can be manually broken out to provide a clear and unimpeded evacuation path.

        - [The power operated sliding doors shall be electro-mechanically locked in position.]

          - Upon release of the electro-mechanical locking device, the sliding doors shall automatically slide to the full open position.

  - HARDWARE

    - Two Wing Revolving Door Entrances:

      - Locking System:

        - The revolving door will automatically cycle and rest in the full closed and lock position when the selector switch is placed in position #1.  This locking system utilizes the magnetic brakes and motor drive units and is controlled by the (MCU) Master Control Unit.

        - Two (2) rotating brakes shall provide instantaneous braking of the revolving door.

        - [Electro-mechanical lock shall set a hardened 1/2 diameter dead bolt between the fixed wall structure and the rotating door sections of the revolving door.]

          - The electro-mechanical lock must be completely automatic and must be controlled by the MCU through the selector switch.

  - ALUMINUM FINISHES

- NOTE:  Consult SpecDesk for custom finish options

    - Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

    - Curved Enclosure Finish:

      - [Anodized Finish:]

        - [AAMA 611, Clear, AA- M12C22A41, Class I, 0.018 mm.]

        - [AAMA 611, Dark Bronze, AA-M12C22A44, Class I, 0.018 mm.]

        - [AAMA 611, Custom anodized to match architect’s sample.]

      - [Painted Finish:]

        - [Powder coat painted to match architect’s sample.]

        - [Kynar finish, [2 coat]  [3 coat], to match architect’s sample.]

      - [Clad Finish (protective coatings by others):]

        - [Stainless steel with #4 satin finish.]

        - [Stainless steel with #8 mirrorlike, reflective, non-directional finish.]

        - [Bronze with a satin finish.]

        - [Bronze with a polished, non-directional finish.]

        - [Brass with a satin finish.]

        - [Brass with a polished, non-directional finish.]

      - [To match architects sample.]

- NOTE:  Typically the curved enclosure (above) and the rotating enclosure (below) are specified to receive the same finish

    - Rotating Enclosure Finish:

      - [Anodized Finish:]

        - [AAMA 611, Clear, AA- M12C22A41, Class I, 0.018 mm.]

        - [AAMA 611, Dark Bronze, AA-M12C22A44, Class I, 0.018 mm.]

        - [AAMA 611, Custom anodized to match architect’s sample.]

      - [Painted Finish:]

        - [Powder coat painted to match architect’s sample.]

        - [Kynar finish, [2 coat]  [3 coat], to match architect’s sample.]

      - [Clad Finish (protective coatings by others):]

        - [Stainless steel with #4 satin finish.]

        - [Stainless steel with #8 mirrorlike, reflective, non-directional finish.]

        - [Bronze with a satin finish.]

        - [Bronze with a polished, non-directional finish.]

        - [Brass with a satin finish.]

        - [Brass with a polished, non-directional finish.]

      - [To match architects sample.]

- NOTE:  Include a roof finish if required for the project

  - CEILING FINISH

- NOTE:  Consult SpecDesk for custom finish options

    - Ceiling Panel Finish:

      - [White laminate faced insulation board.]

      - [Colored laminate faced insulation board panels.]

      - [Stainless steel laminate faced insulation board panels.]

      - [Anodized clear aluminum laminate faced insulation board panels.]

- EXECUTION

  - EXAMINATION

    - Examine the opening to receive the revolving door entrance with the Installer present, for compliance with requirements for installation tolerances, wall and floor construction, and other conditions affecting performance.

    - Examine roughing-in for electrical source power to verify actual locations of wiring connections.

    - Proceed only after such discrepancies or conflicts have been resolved.

  - INSTALLATION

    - Do not install damaged components.  Fit frame joints to produce hairline joints free of burrs and distortion. Rigidly secure non-movement joints.  Seal joints watertight.

    - Entrances:  Install revolving door entrances plumb and true in alignment with established lines and grades without warp or rack of framing members and doors.  Anchor securely in place.

      - Install revolving door entrances in accordance with manufacturer’s printed instructions and recommendations.

      - Install surface mounted hardware using concealed fasteners to greatest extent possible.

      - Install components to drain water passing joints, condensation occurring within framing members, and moisture migrating within the assembly to exterior.

    - Door Operators:  Connect door operators and lighting to electrical power distribution system as specified in Division 26 Sections.

    - Glazing:  Glaze revolving door entrances in accordance with the Glass Association of North America (GANA) Glazing Manual, published recommendations of glass product manufacturer, and published instructions of automatic entrance system manufacturer.

    - Sealants:  Comply with requirements specified in division 7 Section “Joint Sealants” to provide a weather tight installation.

      - Set sill members, flashings, and framing members in full bed of sealant.

      - Seal perimeter of framing members with sealant.

    - Signage:  Apply signage on both sides of each door as required by ANSI/BHMA A156.27 and manufacturers installation instructions.

  - ADJUSTING

    - Adjust door operators, controls and hardware for smooth and safe operation and for weather tight closure. Adjust doors in compliance with ANSI/BHMA A156.27.

  - FIELD QUALITY CONTROL

    - Before placing doors into operation, AAADM certified technician shall inspect and approve doors for compliance with ANSI/BHMA A156.27.  Certified technician shall be approved by the manufacturer.

  - CLEANING AND PROTECTION

    - Clean adjacent surfaces soiled by door installation.

    - Clean glass and metal surfaces promptly after installation. Remove excess sealants, compounds, dirt and other substances. Repair damages to match original finish.

  - DEMONSTRATION

    - Engage a factory-authorized representative to train Owner's maintenance personnel to adjust, operate, and maintain safe operation of the revolving door entrance.

END OF SECTION